## Home
Click on Shortcuts
PcVue Features&Limitations | This document contains some known figures and limitations in PcVue. As standards, specifications and designs change from time to time, please ask our technical support for confirmation of the information given as indication in this document. Arc Informatique shall have no liability whatsoever with respect to information contained herein.
PcVue Version | 16
Last update | August 2022
STATUS | Public
Version | 9
Updates
Aug 2022 | Add video
Feb. 2022 | Add users tab
Dec 2021 | Add SnapVue known limitations
2021-11-01 | Add HDS benchmarks
PcVue
Features & limitations
Data acquisition
Archives
HDS benchmark
Variables
Graphics
Actions
Network
WebVue
Webservices
TouchVue
WebVue
SnapVue
Users
Videos

## Data acquisition
BACK HOME
PcVue Features&Limitations
COMMUNICATION
Drivers |  |  | Comment
Drivers for the machine builders and the industry
Serial |  |  |  | Legend
Maximum recommended number of comm ports | 64 |  |  | Values displayed in red :
Ethernet | Modbus TCP/IP Master | SIEMENS IP-ISO S7 S7 Master |  | Theorical or recommended maximum value, under certain conditions this limit may be different . Contact your technical support for more information.
Maximum recommended number of Networks per configuration | 128 | 128
Maximum recommended number of Nodes per configuration | 1024 | 1024
OPC | OPC DA Client | OPC XML Client
Maximum recommended number of OPC servers that can be configured | 10 | 10
Maximum recommended number of OPC groups that can be configured | 50 | 50
Drivers for Power System Automation
IEC | IEC61850 Client | IEC 60870-5-104 Client
Maximum recommended number of IED | 300 | 300
DNP3 | DNP 3.0 Client
Maximum recommended number of IED | 300
Drivers for Building Management Systems
LonWorks | Lon Client
Maximum recommended devices | 300
BACnet | BACnet Client
Maximum recommended devices for a number of data per device in COV mode | 1000 (50 data/devices)
Maximum recommended devices for a number of data per device in pollling mode | 2000 (50 data/devices) Polling > 1min |  | Depend on var type and network performances
SNMP | SNMP Manager |  | Available in V11.1 and later
Maximum devices | 1000

## Archives
BACK HOME
PcVue Features&Limitations
ARCHIVES
Topic | Values |  |  | Comments
HDS
HDS SQLServer archive units | Min | Max | Default
Number of archive units that can be configured | - | 512 | -
Number of databases | 1 | 10 | -
Number of tables (all databases included) | 1 | 1000 | -
Number of historical trends | - | 100000 | -
Number of historical event logs | - | 300000 | -
HDS SQLServer performances | Min | Max | Default
Number of incoming events buffered for treatment by the HDS that can be configured (MaxBufferEvents) | 20000 | 200000 | 20000 | When HDS has more events it stops accepting new events from external source while its buffer list is saturated This value should be set to a value of 20% above the nominal recorded events flow
Number of events in the writing buffer that can be configured (MaxBookmarkInTable) | 40 | 500 | 40 | When the number of event is reached, the buffer is triggered to be written in the database. Values given for a stable system recording 5100 events/s
Number of records to delete in one time during a purge maintenance task (DefaultMaxPurgedRecords) | 30000 | 60000 | 30000
Number of trend/logs values recorded per second | 400
Start up time with 100 000 historical trends | 163 s
Number of log values recorded per second | ?
| HDD | RAID 10 with embedded cache configuration |  | Software configuration - Windows Server 2008 R2 Enterprise SP1 x64 - SQL Server 2008 x64 installed on system disk Common hardware configuration - CPU : Intel Xeon E31220 @ 3.10GHz - RAM : 8GB Optimized configuration : Data file (.mdf) and Log file (.ldf) split on 2 disks
Number of records written per second in a continuous mode (writes only,no read, and no maintenance) | 2500 | 5100 |  | The expected performances are dependent of parameters such as number of connected stations, PLC communication, operators’ activity, Database purge policy and more. Please contact your technical support for more details.
Purge duration for 6,5Gb of data (1h at 3700 events/s) | 50 minutes |  |  | Same configuration as above MaxBufferEvents = 200 000 MaxBookmarkInTable = 100 DefaultMaxPurgedRecords = 30 000
Proprietary archive units | Min | Max | Default
Number of unit | - | 512 | -
Capacity per archive unit | 1 MB | 100 GB* | 10 MB | * expressed in the Archive Unit properties dialog as 100000 MB.
Capacity per file | 1 KB | 32 MB** | 1000 KB | ** expressed in the Archive Unit properties dialog as 32000 KB.
Number of historical trends | - | 60000 | -
Number of trend values recorded per second | - | 10000 | -
Number of log values recorded per second | - | 10000 | -
Number of historical event logs | - | 60000 | -
Trends cache memory size | 1 KB | 32 KB | 32 KB | Cache memory size - The size of the memory buffer used. If set to zero then it is disabled.1 | 1 See online help topic Trend Recording Advanced Options
Trends cache write period | 0 sec. | 32000 sec. | 120 sec. | Cache write period - The frequency at which the cache is flushed to HISTO.SAV1
Trends filtering period | 0 sec. | 32000 sec. | 0 sec. | See online help topic Understanding How the Trend Period Affects Recording
Log list cache memory size | 1 KB | 32 KB | 32 KB | Cache memory size - The size of the memory buffer used. If set to zero then it is disabled2 | 2 See online help topic Log List Advanced Configuration
Log list cache write period | 0 sec. | 32000 sec. | 120 sec. | Write period - The frequency at which the cache is flushed to HISTO.SAV.2
Log list time ordered buffer period | 0 sec. | 32000 sec. | 0 sec. | Period - The period for which data is sorted. If this is zero then no sorting takes place2
Log list time ordered buffer size | 1 KB | 900 KB | 900 KB | Memory size - The size of the memory buffer used to sort data before it is copied to disk. 2
Reports cache memory size | 1 KB | 32 KB | 32 KB
Reports cache write period | 0 sec. | 32000 sec. | 120 sec.
Free archive units | Min | Max | Default
Cache memory size | 0 KB | 32 KB | 32 KB
Cache write period | 0 sec | 32000 sec | 120 sec
Capacity per file | 0 KB | 32000 KB | 0 KB
VCR
Reports | Min | Max | Default
Cache memory size | 1 KB | 32 KB | 32 KB
Cache write period | 0 sec. | 32000 sec. | 120 sec.
VCR Unit | Min | Max | Default
Unit size | - | 100 Go | -
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## HDS benchmark
BACK HOME
PcVue Features&Limitations
ARCHIVES | HDS BENCHMARK
Machine caracteristics
Disk 1 | SSD 512 | kingston skc400s37512g
Disk 2 | SSD 256 | kingston skc400s37256g
Network | PcVue and SQL Server on 2 separated machines
Version | MaxBookmarkInTable | avg time per record (s) | PendingRecordPeriod (default) (s) | SQLServer requirement :
15.2 | 40 | 0.55175 | 10 | N* MaxBookMark<2100
| 100 | 0.5599 | 10 | N=Number of columns created in the database associated to the variable properties
| 200 | 0.50895 | 10
| 500 | 0.45798 | 10
Local | PcVue and SQLServer on the same machine
Version | MaxBookmarkInTable | avg time per record | PendingRecordPeriod (default) (s)
15.2 | 40 | 0.29475 | 10
| 100 | 0.5596 | 10
| 200 | 0.42962 | 10
| 500 | 0.59607 | 10
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## Variables
BACK HOME
PcVue Features&Limitations
VARIABLES
Topic | Value | Comment
Variables
Maximum number of variables for a project including I/O | 300000
Maximum number of characters for a full branch, including any full stops used to separate sub-branches | 253
Maximum number of characters for a variable name (including its branch) | 255
Maximum number of branch levels for a variable | 12
Maximum number of characters for variable description | 255
Memory size for a bit | ?
Memory size for a Register | ?
Memory size for a Text | ?
Type of characters supported |  | Alphanumeric and underscore character
Levels
Maximum number of alarm acknowledgment levels | 30
Maximum number of control levels | 30
Maximum number of alarm masking levels | 30
Domain/Nature
Maximum number of Domain/Nature | 512
Maximum number of alphanumeric characters for a Domain/Nature | 100
Text attributes
Maximum number of text attribute per variable | 16
Maximum number of characters for a text attribute | 100
Maximum number of binary attribute per variable | 1
Binary attributes
Maximum number of binary attribute per variable | 32?
Expressions
Max length of expression name | 256
Maximum number of expressions on a variable that can be configured. | 49152
Maximum number of expressions that can be active in an open mimic. (Entered directly in an animation instead of a variable name) | 49152
Maximum number of symbols in an expression | 125
Recipes
Maximum number of recipes that can be configured | 49152
Maximum number of variables for a recipe | 2000
Population filters |  | A Population is a filter which may be applied to the variables tree of a station to control the distribution of variable values. Variables can be included in, or excluded from a Population using the following criteria : By Domain. By Nature. By the variable type, Bit, Alarm, Register or Text. By the source of the value, Internal, External, Equipment, DDE or Broadcast See online help topic Population Filters
The maximum number of Populations that may be created | 512
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## Graphics
BACK HOME
PcVue Features&Limitations
GRAPHICS
Topic | Value | Comment
Color palette
Number of normal colors in the palette | 248
Number of indexed colors in the palette | 248
Images
Rotation of png | No
Layers
Maximum number of layers | 16
Mimics
Maximum number of simultaneously opened mimics | 100 | The best practice is to avoid having too many simultaneously opened mimics
Maximum number of access levels | 30
Maximum size (pixels) of a mimic | 10000 x 10000
Zoom levels | 0 to 6400
Libraries
Maximum number of libraries | 255
Animations
Maximum number of animation for an object | 32
Maximum objects supported in a mimic
2D objects
3D objects
TrendViewer
AlarmViewer
LogsViewer
ActiveX
GIS markers
Incrustated mimics
Number of child mimics
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## Actions
BACK HOME
PcVue Features&Limitations
ACTIONS
Topic | Value | Comment
Event actions
Maximum number of events that can be configured | 32000
Cyclic actions
Max length for cyclic action name | 256
Maximum number of cyclics that can be configured | 512
Minimu period for a cyclic action | 1s
SCADA Basic programs
Max size of each program | 640 000 bytes
Max number of symbols per program | Unlimited | Symbols : Working variables,verb, logical operators
Max number of programs (global included) | 60
Max length of the STR variable | 512
Max number of arguments for verbs | 18
Max number of declares for DLL | 50
Max number of arguments for DLL | 16
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## Network
BACK HOME
PcVue Features&Limitations
NETWORK
Topic | Value | Comment
Number of station that can be configured | 256
Number of station within an association that can be configured | 5
Number of associations that can be configured | 10
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## WebVue
BACK HOME
PcVue Features&Limitations
WebVue
Topic | Value | Comment
Number of simultaneously WebVue clients | 50
Number max of graphic objects in a mimic displayed on WebVue | 5000
Limitations
The following animation types are not supported:
Grid Display
Recipe
Region
Timetable
The use of substitution strings for opening mimics is not supported (#I, #P, #U, #M1 to #M20).
The form controls are supported but their appearance is slightly different due to the run-time environment (Java instead of Microsoft Windows). The intermediate state of a check box or radio button form control is not available. You cannot use variables with Form Controls for mimics displayed in WebVue.
The Trend, Alarm and Log Viewers have some limitations on their functionality.
AVI (multimedia) files are not supported.
If a mimic is repeated in the Supervisor's Workspace, only the first instance appears in the WebVue Client.
The options available when entering a text string or register value are limited.
There is limited support of pop-up (child) mimics.
Limited use of function keys.
The Zoom function is not available.
There is limited support of fonts and styles. Fonts will generally be supported if they are installed both on the Supervisor's station and on the browser of the WebVue Client's station. The fonts Arial, Courier, Times New Roman, and System are widely supported.
Regular, italic and bold styles are supported; underline styles are not.
Control zone animation accelerator keys are not supported.
ActiveX controls in mimics are not supported.
OLE objects in mimics are not supported.
VBA and Enable scripts not supported.
Limited support for SCADA Basic instructions and modes.
3D mimics not supported.
The substitution characters for opening windows are not available (#I, #P, #U, #M1 to #M20, as documented in Using Substitution Characters).
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## WebServices
BACK HOME
PcVue Features&Limitations
Web services
Topic | Value | Comment
Number maximum of simultaneously Webservices clients | 50
Number maximum of alarms subscribed for 1 connexion (network speed >100 Mb) | 5000 | Beyond this value a server (JBOSS,MVC,…) should be used as a gateway
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## TouchVue
BACK HOME
PcVue Features&Limitations
TouchVue
Topic | Value | Comment
Number of sub item within a branch | 300 | Depends on the hardware ressources
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## SnapVue
BACK HOME
PcVue Features&Limitations
SnapVue
Topic | Value | Comment
Number of zone that can be configured | Unlimited
Number of geotags that can be configured | Unlimited
Number of actions that can be configured in server/visible in the client | Unlimited/80
Number of tiles that can be configured in server/visible in the client | Unlimited/80
Number of trends that can be configured | 16
Number of lines of messages visible in a messaging viewer of the client | 100
Number of state for a BOT | 50
Number of operation possible in state (BOT) | 100
Number of conditions in a transition (BOT) | 100
Maximum amount of simultaneous users (Peak) | 144
Maximum amount of simultaneous users (Nominal) | 300
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## Users
BACK HOME
PcVue Features&Limitations
USERS
Topic | Value | Comment
Number of users that can be configured | Unlimited
Number of user profiles that can be configured | Unlimited
Number of users that can be imported from Active Directory | Unlimited | 10 000 users using profiles require 20Mo of RAM 20s of loading time
When connecting to an Active Directory, do the imported users saved locally in cache memory? | Yes | Informations associated to the connected user are saved and available via the variable s"SYSTE" of PcVue
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.

## Videos
BACK HOME
PcVue Features&Limitations
Video control
Topic | Value | Comment
File format supported | *.avi *.mp4 *.mp2 *.wmv
fps max | Depends on the device
Time to connect and dispay the video when using the component running on a VM | 8-15s
Legend Values displayed in red : Theorical or recommended maximum value, under certain conditions this limit may be different .
Contact your technical support for more information.